Text for tender for water connection kit top/bottom, 3311.040

for TopTherm LCP CW 3311.130/230/260/530/560

Water connection kit top/bottom:

The water connection kit makes it easy to connect the LCP to existing pipework.

By means of a flexible hose size deviations may be compensated and simultaneously the LCP can be decoupled from the pipework.

Due to the hose length of 1.8 m the medium connection into the LCP can be made from the bottom (raised floor) or from the top.

Water connection kit top/bottom, supply includes:

Two Carboflex hoses (inlet/return), resistant against water and anti-freeze agent
Insert made from steel wire spiral and copper litz wire.

Internal diameter: DN 32

Length: 1800 mm

Operating pressure 16 bar at 30°C

Temperature range -20°C to +80°C

Connection side to LCP:
G 1 ½“ union nut, flat sealing, SW 46

Connection side to existing pipework:
G 1 1/4“ union nut, flat sealing, SW 46

The length of the hose may be shortened on site by two removable half-shells.