Tender text for TopTherm LCP Inline CW, 3311.560 WHD (mm) 300x2000x1200

TopTherm LCP Inline CW:

The design of the unit is optimised for use in data centres. The integrated air/water heat exchanger guarantees a cooling output of up to 60 kW, combined with standard server enclosure dimensions, the lowest possible weight and comprehensive possibilities for monitoring.

The air/water heat exchanger is mounted on the side of the rack.

LCP Inline draws the hot server air in via a perforated rear door.

The front of the unit protrudes approx. 200 mm in front of the server racks; the cooled air is expelled left and right, over the whole enclosure height, in front of the perforated doors of the server racks and is thus made available to the 482.6 mm (19") equipment once more.

The use of four integrated EC fan modules (cooling output up to 40 kW) achieves maximum efficiency and minimises the electrical energy consumption.

The unit is prepared for the incorporation of a maximum of six EC fan modules (cooling output up to 60 kW). For this reason it is possible to retrofit two additional fan modules up to full configuration and achieving the optimum cooling output.
This safeguards the value of an investment where the full cooling output is not yet required at the time of initial operation.

The flow characteristics of the heat exchanger have been optimised for the minimum possible pressure loss on the air side. This in turn minimises the energy consumption of the fans.
The high-performance heat exchanger guarantees maximum cooling output even at high water inlet temperatures, enabling the proportion of operation in combination with indirect free cooling to be maximised and operating costs reduced accordingly.

The air/water heat exchanger and server rack remain separate from each other. This eliminates the risk of water penetrating into the server rack and improves the ease of installation and service.

Leakage management is integrated.

The water connection can be realised optionally to the top or bottom by way of an accessory kit 
(1 1/2“ thread).
Fast commissioning of the unit thanks to fast and simple air bleeding.

The standard integrated software/controller concept provides for automatic control of the specified server air intake temperature. The fan speed and cooling water flow rate are both infinitely variable, for precise matching to the power losses of the components installed in the IT rack.

The optimum operating point is thus achieved with minimum energy consumption and correspondingly reduced operating costs.

An intelligent sensor network monitors the air and water temperatures, as well as the water flow rate and leakage management.
The incorporation of three temperature sensors for the hot and cold air provides for redundancy. An integrated fail-safe mode, furthermore, ensures reliable cooling, even in case of failure of the electronics.

The monitoring and alarm management for all physical parameters is realised via SNMP and Ethernet. A BACnet link is possible as an option.

New control algorithms permit energy-efficient operation and take into account the demands of facility management.

To enable the displaying of all physical parameters, an optical colour touchscreen can be integrated into the front of the unit.

The optimised layout provides for fast and simple maintenance and service for all relevant components. The fans can be exchanged at any time in a matter of seconds, also during operation (hot swapping).
The temperature sensors in the water inlet/return are integrated into thermowells and can similarly be exchanged without interrupting operation.

Technical specifications:

- Adaptable cooling output with four/five/six fans: 40/45/55kW (60kW on request)

- Installed fans: 4

- Air throughput: 8000 m³/h (six fans)

- Cooling output (six fans): 55kW (60kW on request)

- Air intake temperature: max. 25°C

- Water inlet temperature: 15°C

- Medium: Water

- Coolant throughput: approx.125l/min

- Pressure loss: approx. 1bar

- Voltage: 208/230 V, 1~, 50/60 Hz, 400 V, 3~, N, 50/ 60 Hz

- Max. connected load (six fan modules): 2800 W

- Server air intake temperature maintained by way of flow rate control and EC fans with infinitely variable speed

- Colour: RAL 7035

Usable installation height: free (standard: 42 U)

Dimensions: WxHxD: 300 x 2000 x 1200 mm

Weight: approx. 230 kg

Optional:

Fan module for capacity expansion: 3311.011

Touchscreen display, colour: 3311.030

Connection hose, bottom/top: 3311.040

Adaptor for 3311.530/560: 3311.080

Schematic representation