Edition 16.01.2013		NEWAVE/ABB DPA UPScale Modular UPS

GUIDE SPECIFICATIONS (DPA UPScale: Total power 10 to 200 kW)

for DPA UPScale  M-10-, M-20 kW UPS Modules
(400/230V, 415/240V or 380/220V)

Three-Phase Uninterruptible Power Supply System

1.0 GENERAL

1.1	SCOPE

The Uninterruptible Power Supply (UPS) systems are required to provide continuous, regulated AC power to the equipment of The Organisation, irrespective of any disturbances or disruptions occurring on the main power supply.

This specification describes the NEWAVE/ABB DPA UPScale modular UPS, a modular uninterruptible power supply system for data centre, network, telecom and other critical equipment applications. It defines the electrical and mechanical characteristics and requirements for a continuous-duty three-phase, solid-state, uninterruptible power supply system. The uninterruptible power supply system, hereafter referred to as the UPS, shall provide high-quality AC power.

1.2	STANDARDS

The UPS shall be designed in accordance with the applicable sections of the current revision of the following documents.  Where a conflict arises between these documents and statements made herein, the statements in this specification shall govern.

| Safety Standard: | IEC/EN 62040-1 |
| --- | --- |
| Electromagnetic Compatibility Standard (EMC) | IEC/EN 62040-2 Emission Class C2 Immunity Class C3 |
| Performance Standard: | EN 62040-3 |

1.3	SYSTEM DESCRIPTION

    - General

1.3.1.1	Parallel Installation

1.3.1.2	Capacity (non-redundant) system.

All the UPS units connected in parallel are required to supply the full rated load within the same cabinet. If a UPS power unit or control module should malfunction, the load is to be transferred automatically to the bypass line via each of the UPS units with their static bypass switches being triggered simultaneously.  The battery set should consist of at least two strings so that in the event of a battery malfunction the affected string is automatically isolated from the system thereby ensuring battery autonomy is retained, albeit of a shorter duration.

1.3.1.3	Redundant operation

The UPS system will operate in an N+n configuration where N is the number of UPS units connected in parallel to support the load and n is the number of UPS units connected in parallel to provide the co-efficiency of redundancy.

The parallel UPS units shall be capable of operation from a common DC bus or with a separate DC supply for each UPS unit.  In either case the batteries should be configured so that the failure of one battery string (common DC bus) or the failure of one battery set (separate DC supply for each UPS) provides battery redundancy whereby the specified autonomy at full load is maintained.

The malfunction of one of the UPS unit’s power or control modules shall cause that particular UPS unit to be automatically isolated from the system and the remaining UPS units shall continue to support the load.  Replacement or repair of a UPS unit shall be achieved without disturbance to the connected load, while the remaining modules continue operating in online mode (online safe swappability)

1.3.2	Modes of Operation

The UPS shall be designed to operate as a true on-line, double conversion Voltage and Frequency Independent (VFI) system in the following modes:

A.	Normal - The critical AC load is continuously supplied by the UPS inverter.  The input converter derives power from the utility AC source and supplies DC power to the inverter.  The battery charger shall maintain a float-charge on the battery.

B.	Battery - Upon failure of utility AC power the critical AC load is supplied by the inverter, which obtains power from the battery. There shall be no interruption in power to the critical load upon failure or restoration of the utility AC source.

C.	Recharge - Upon restoration of utility AC power, after a utility AC power outage, the input converter shall automatically restart and resume supplying power to the inverter.  Also the battery charger shall recharge the battery.
In addition to the input conversion soft start of each UPS module, when a mains recovery occurs, all single input converters shall switch on in a sequential way with a delay of about 5 seconds from each to the other module within the system configuration.

- Automatic Restart - Upon restoration of utility AC power, after a utility AC power outage and complete battery discharge, the UPS shall automatically restart and resume supplying power to the critical load on inverter.

E.	Bypass - The bypass shall provide an alternate path for power to the critical load that shall be capable of operating in the following manner:

1.	Automatic - In the event of an internal failure or should the inverter overload capacity be exceeded, all UPS modules shall perform an automatic transfer of the critical AC load from the inverter to the bypass source.

2.	Eco-Mode – The UPS module(s) shall be able to operate in Eco-Mode when the power quality parameters of the by-pass source are within the permissible tolerances. The UPS system shall automatically transfer the load to normal mode if the by-pass source goes out of permissible tolerances. Transfer in both directions shall take place very rapidly (< 5ms) and shall not affect the supplied load.

3.	Manual - Should the UPS module(s) need to be taken out of service for limited maintenance or repair, manual activation of the bypass shall cause an immediate transfer of the critical AC load from the inverter to the bypass source.

1.3.3	Performance Requirements

	A. 	The UPS shall be a true on-line double conversion, voltage and frequency 		independent (VFI) technology in accordance with 
		standards EN 62040-3

1.3.3.1	AC Input to UPS

| Nominal Input Voltage | V | 3x380/220V+N, 3x400V/230V+N, 3x415/240V+N |
| --- | --- | --- |
| Input Voltage Tolerance (ref to 3x400/230V) for Loads in %: | V | (-23%/+15%) 3x308/177 V to 3x460/264 V for <100 % load (-30%/+15%) 3x280/161 V to 3x460/264 V for < 80 % load (-40%/+15%) 3x240/138 V to 3x460/264 V for < 60 % load |
| Input Frequency | Hz | 35 – 70 |
| Input Power Factor |  | PF=0.99 @ 100 % load |
| Inrush Current | A | limited by soft start / max. In |
| Input Distortion THDI |  | Sine-wave THDi = < 3 % @ 100% load |

1.3.3.2	AC Output

| Output Rated Voltage | V | 3x380/220V or 3x400/230V or 3x415/240V |
| --- | --- | --- |
| Output Voltage Stability | % | Static: < +/- 1% Dynamic (Step load 0%-100% or 100%-0%) < +/- 4% |
| Output Voltage Distortion | % | With Linear Load < +/- 1.5% With Non-linear Load (EN 62040-3) < +/- 4% |
| Output Voltage Stability | % | Static: < +/- 1% Dynamic (Step load 0%-100% or 100%-0%): < +/- 4% Bypass operation: +/- 15% |
| Output Frequency | Hz | 50 Hz or 60 Hz |
| Output Frequency Tolerance | % | Synchronized with mains < +/- 2 % (selectable for bypass operation) or < +/- 4 % Free running +/- 0.1 % |
| Permissible Unbalanced Load | % | 100% |
| Phase Angle | Deg. | +/- 0 deg. |
| Overload Capability on Inverter | % | 125 % load 10 min. 150 % load 60 sec. |
| Output short capability (RMS) | A | Inverter : 3 x In during 40 ms Bypass : 10 x In during 20 ms |
| Crest - Factor |  | 3 : 1 |

1.3.3.3  UPS Efficiency
 
			The typical overall efficiency (AC/AC, on-line mode) 	
			shell be > 95.5 %

1.3.3.4	Batteries

A	The battery system shall be sized to support a connected load of XXX kW for a minimum of XX minutes at an ambient temperature 
of 25 °C.

The battery system shall consist of gas recombination, valve regulated, lead acid cells, Flame retardant batteries shall be provided, which renders the UPS suitable for installation inside a computer room.

The UPS shall contain provisions to fit additional battery modules internally if space permits. The UPS shall also interface with an external battery cabinet to extend reserve time capabilities.

C	The UPS battery charging circuit shall comprise of a separate battery charger and not depend on a charge voltage being derived from the UPS input rectifier.  Consequently the battery charging voltage shall have zero AC (ripple) content.

D	For single UPS systems the battery system shall consist of a minimum of 1 strings of multiple cells.

For multiple UPS units connected in parallel the battery system shall be either:

A separate battery system for each individual UPS module.  In this case each separate battery system may consist of one protected string of multiple cells.

or
A common battery feeding all the UPS units.  In this case the battery system shall consist of a minimum of two parallel strings of multiple cells.  Each individual string shall have its own dedicated means of electrical circuit protection.

For all the above battery system arrangements the batteries shall be configured so that in the event of a battery malfunction the affected string is automatically isolated from the system thereby ensuring battery autonomy is retained

E	The batteries shall be housed in cabinet/s comprising a floor-standing steel enclosure with dimensions and paint finish to match the UPS system cabinet/s to form a continuous suite when standing immediately adjacent to the UPS system cabinet/s.  The battery cabinet/s shall have full width opening doors to permit ease of access for the purposes of maintenance and/or repair of the batteries.

F	A fully discharged battery system shall be capable of being recharged to 80% of the UPS output capacity within a maximum period of 10 times the normal total discharge time period.

G	The UPS DC bus voltage shall be variable whereby the number of battery blocks can be adjusted between 30 to 50 (12 Vdc blocks) or 60 to 100 ( 6 Vdc blocks) depending the power range and to enable the battery system to be optimised for size and cost.

1.4	ENVIRONMENTAL CONDITIONS

1.4.1	The UPS system shall be designed to operate continuously at full load without degradation of its reliability, operating characteristics or service life in the following environmental conditions:

- UPS operation ambient temperature range   	0°C to 40°C,

- Battery ambient temperature range   20°C to 25°C

- Humidity (relative) 5 to 95% non-condensing

- Storage: 	UPS -5 deg C to +50 deg °C; 
		Battery -20 deg C to 25 deg °C for maximum 6 months

1.4.2	The UPS system shall be designed for operation in altitudes up to 1000 metres, without the need for derating or reduction of the above environmental operating temperatures.

1.4.3	The audible noise generated by the UPS system during normal operation shall not exceed 70 dBA per cabinet measured at 1 metre from the front of the UPS.

1.4.4	The UPS system shall be able to withstand a minimum 4kV electrostatic discharge without affecting the critical load.

1.4.5	To permit access through a standard single doorway opening, either the width or the depth of the UPS and battery cabinets shall not exceed 800mm.

1.4.6	The UPS system cabinet shall comprise of a floor standing steel enclosure to house the power system, control systems, battery connections and all associated necessary connections for the correct operation of the UPS in accordance with the requirement of the specifications.  All switchgear and interconnections must be adequately protected to enable an isolated section to be safely maintained or repaired whilst the remaining system supports the load.

1.4.7	The UPS system shall be designed to limit the injection of current harmonics in to the incoming utility supply and as such the maximum total input current harmonic distortion should not exceed 3 % THDi when the UPS system is operating at the UPS manufacturer’s specified rating.

1.5	USER DOCUMENTATION

The specified UPS system shall be supplied with one (1) user's manual.  Manuals shall include installation drawings and instructions, a functional description of the equipment with block diagrams, safety precautions, illustrations, step by step operating procedures, and routine maintenance guidelines.

1.6	WARRANTY

The UPS manufacturer shall warrant the UPS against defects in materials and workmanship for one (1) year.  With start-up provided by UPS supplier Global Services, the warranty shall cover all parts and onsite labour for one (1) year.  Maintenance contract packages shall also be available.

1.7	QUALITY ASSURANCE

1.7.1	Manufacturer Qualifications

A minimum of 10 year's experience in the design, manufacture, and testing of solid-state UPS systems is required.

1.7.2	Factory Testing

Before shipment, the manufacturer shall fully and completely test the system to assure compliance with the specification.  These tests shall include operational discharge and recharge tests on the internal battery to guarantee rated performance.

2.0 PRODUCT

2.1	FABRICATION

All materials and components making up the UPS shall be new, of current manufacture, and shall not have been in prior service except as required during factory testing.  The UPS shall be constructed of replaceable subassemblies.

2.1.2	Wiring

Wiring practices, materials, and coding shall be in accordance with the requirements of the EN 62040-1 and other applicable codes and standards.

2.1.3	UPS Cabinet

The UPS system comprised of: power module, battery module, system interconnect module and user interface module housed in a single free-standing enclosure and meets the requirements of IP20. The UPS system shall be designed such that the battery modules may be installed into any module bay in the cabinet and power modules into any module bay in the upper half of the cabinet. The UPS cabinet shall be cleaned, primed, and painted:

Front : Graffiti grey + black (inlets),  Side walls: Graffiti grey

UPS cabinet shall not exceed the following dimensions:

Single cabinet UPS system:  550mm wide, 770mm deep, and 1975mm high.

2.1.4	UPS module

The UPS modules shall be of double conversion, continuous duty (true on-line), plug-in and hot swappable technology, in redundant- parallel operation, accommodated in the UPS system rack/cabinet.  Each UPS module shall consist, basically, of a rectifier/charger, a solid state inverter, a static transfer switch and, preferably, its controller. The incorporation of the UPS controller and /or control panel into every individual module shall be considered as a serious advantage. If one UPS module fails, the UPS system shall have the capability to replace the faulty UPS module without transfer the load on by-pass. UPS modules shall not exceed the following dimensions and weights:

:

UPS module dimensions: 488mm wide, 500mm deep, and 3HU (132mm) high
UPS module weight: 20kW module max. 22 kg. 10kW module max. 19kg.N

2.1.5	Cooling

The UPS shall be forced air cooled by internally mounted fans.

2.2	COMPONENTS

2.2.1	Input Converter

A.	General

Incoming AC power shall be converted to a regulated DC output by the input converter for supplying DC power to the inverter.  The input converter shall provide input power factor and input current distortion correction.

B.	AC Input Current Limit

The input converter shall be provided with AC input over current protection.

C.	Input Protection

The UPS shall have built-in protection against undervoltage, overcurrent, and overvoltage conditions including low-energy surges introduced on the primary AC source and the bypass source. The UPS cabinet shall not contain an input breaker. The customer shall supply an input breaker sized to supply the rated load and to recharge the battery at the same time.

D.	Battery Recharge

To prolong battery life, the UPS shall contain temperature-compensated battery charging. The battery charger shall be ripple-free avoiding premature battery ageing.

2.2.2	Inverter

A.	General

The inverter shall convert DC power from the input converter output, or the battery, into precise regulated sine wave AC power for supporting the critical AC load.

B.	Overload

The inverter shall be capable of supplying current and voltage for overloads exceeding 100% and up to 150 % of full load current.  A visual indicator and audible alarm shall indicate overload operation.  For greater currents or longer time duration, the inverter shall have electronic current-limiting protection to prevent damage to components. The inverter shall be self-protecting against any magnitude of connected output overload.  Inverter control logic shall sense and disconnect the inverter from the critical AC load without the requirement to clear protective fuses. The load shall be transferred to bypass when any of the above conditions are exceeded.

C.	Output Frequency

The output frequency of the inverter shall be controlled by an oscillator.  The oscillator shall hold the inverter output frequency to +/- 0.1% for steady state and transient conditions. The inverter shall track the bypass continuously providing the bypass source maintains a frequency within the user selected synchronization range.  If the bypass source fails to remain within the selected range, the inverter shall revert to the internal oscillator.

D.	Output Protection

The UPS inverter shall employ electronic current limiting.

E.	Battery over Discharge Protection

To prevent battery damage from over discharging, the UPS control logic shall control the shutdown voltage set point. This point is dependent on the rate of discharge.

2.2.3		Display and Controls

A.	General

The front panel shall be a individual panel per module and consist of multiple status LEDs (one for each UPS module), switches, and a two line by twenty character backlit LCD display for additional alarm/configuration information (one for each UPS module). During normal operation (on-line), all mimic display LEDs shall be green in colour and indicate the following:

Line 1 (AC Input rectifier)

Line 2 (AC Input by-pass)

Battery	(Load supplied from the battery)

On Inverter (Load supplied from the inverter)

On Bypass (Load supplied from the by-pass)

The UPS fault indicator is used with additional indicators and audible alarms to notify the user that a UPS fault condition has occurred. During mains failure the colour of the indicator LED shall be as follows:

Line 1 (AC Input rectifier)				red colour

Line 2 (AC Input by-pass)				red colour

Battery	(Load supplied from the battery)		green colour

On Inverter (Load supplied from the inverter)	green colour

On Bypass (Load supplied from the by-pass)	off (no colour)

If there is a fault condition, the UPS shall attempt to maintain conditioned power to the load or at minimum transfer to bypass.

There shall also be indication on each module should the module fail and need to be replaced.

In addition to a visual fault signal (alarm), the UPS shall also record fault occurrences in a rolling event log. The event log on the standard unit shall record up to 99 occurrences, with the oldest events discarded first, etc. The user shall have access to the event log through the LCD display. Every alarm and/or event recorded in the event log will contain a time and date stamp.

B.	Audible Alarms

The volume of all audible alarms shall be at least 65dBA at a distance of one meter. An audible alarm shall be used in conjunction with the LED/LCD indication to indicate a change in UPS status.

The audible alarms shall warn for utility line loss, low battery (while on battery), and all other alarm conditions. For all alarm conditions, the user must look at the display to determine the cause of error/alarm. All alarm tones shall be a continual tone until the condition rectifies itself or the alarm is silenced. Once silenced, the audible alarm shall not sound until a new alarm condition is present, but the LED indication still warning the alarm condition.

C.	Alarm Silence Button

In addition to the double load on/off switch, the user interface shall include an audible ‘Reset’ switch. If the alarm silence (Reset) switch is pressed for one second, all current audible alarms shall be disabled. If a new alarm occurs, or a cancelled alarm condition disappears and then re-appears, the audible alarm is re-enabled.

D.	LCD Display

The LCD display shall be used to provide information to the user. The display shall be able to provide the following measurements information:

Voltages:   Input converter 	(Phase 1-2-3/Neutral)

Input by-pass 	(Phase 1-2-3/Neutral)
	     UPS output 		(Phase 1-2-3/Neutral)

Battery

Current:     UPS output 		(PH1-2-3)
	     Battery charging/discharging

Frequency:UPS Input

UPS output

Battery:	     Remaining back-up time (minutes)
	     Capacity (%)

Others:	     UPS output active power (kW), 	(Phase 1-2-3/Neutral)

UPS output reactive power (Kvar), 	(Phase 1-2-3/Neutral)
	     UPS output apparent power (kVA), 	(Phase 1-2-3/Neutral)
	     UPS load (%), 			(Phase 1-2-3)

2.2.4	Automatic Battery Test

The UPS shall initiate an automatic battery testing sequence periodically (once a month), at a programmed day and time of day, selectable by the end user. The user will be able to able and disable the automatic battery test.

Should a failure of the battery occur, the UPS will immediately return to normal mode and fault signals (visual, audible, and remote via serial) shall be communicated. No audible or remote (via serial/contact closures) indication of the battery test shall be communicated during the duration of the automatic battery test.

The automatic battery test shall be able to operate only if no alarms conditions affect the UPS and if the battery is at least 90% of its full capacity.

2.2.5	Remote shut down

The remote shut down function shall allow the user to disable all UPS (Modules) outputs in an emergency situation. The Remote shut down shall be able to interface with normally closed (N.C.) systems. The Remote shut down shall be activated when a pair of ‘SELV’ contacts, external to the UPS, are activated. The Remote shut down connection shall be through a simple terminal block type connector.

The Remote shut down function shall not operate if no system control modules are present in the UPS or if the manual bypass switch is in the bypass position. The user must also supply a means of interfacing with the Remote shut down circuit to allow disconnecting the UPS input feeder breaker to remove all sources of power to the UPS and the connected equipment to comply with local wiring codes/regulations.

2.2.6	Gen-on contact

		A diesel-genset contact shall be provided in order to:
		- reduce the battery charging (programmable)
		- lock the by-pass transfer (programmable)

2.2.7	Bypass

A.	General

A bypass circuit shall be provided as an integral part of the UPS module. The bypass control logic shall contain an automatic transfer control circuit that senses the status of the inverter logic signals, and operating and alarm conditions. This control circuit shall provide a transfer of the load to the bypass source, without exceeding the transient limits specified herein, when an overload or malfunction occurs within the UPS.

B.	Automatic Transfers

The transfer control logic shall automatically activate the bypass, transferring the critical AC load to the bypass source, after the transfer logic senses one of the following conditions:

Inverter overload capacity exceeded

Inverter over temperature

UPS fault condition (non redundant configuration)

For inverter overload conditions, the transfer control logic shall inhibit an automatic transfer of the critical load to the bypass source if one of the following conditions exists:

Inverter/Bypass voltage difference exceeding preset limits 
(-20/+15 % of nominal load @ 100 % load)

Bypass frequency out of preset limits (± 4 % or  +- 2 % of nominal frequency)

C.	Automatic Retransfer

Retransfer of the critical AC load from the bypass source to the inverter output shall be automatically initiated unless inhibited by manual control.  The transfer control logic shall inhibit an automatic retransfer of the critical load to the inverter if one of the following conditions exists:

Bypass out-of-synchronization range with inverter output

Overload condition exists in excess of inverter full load rating

UPS fault condition present (non redundant configuration)

D.	Manual Transfer

In addition to the internal bypass function, the UPS shall have a manual bypass function. The manual bypass function shall be provided via a switch mounted on the bottom-front of the UPS, removal of the lower front bezel shall be required. 

In case of wrong manual by-pass manipulation (transferring the load on manual by-pass when the load is supplied by the inverter (Normal-mode)), the UPS module(s) shall be auto protected avoiding any UPS damage.

The UPS shall initiate an audible alarm upon transfer to manual bypass. The audible alarm shall be capable of being silenced by the user. The alarm shall continue to sound (unless silenced) while in bypass mode. This shall provide a reminder to the user that the load continues to be powered from utility supply alone.

2.2.8	Internal Battery

Flame retardant, valve regulated, gas recombination, lead acid batteries shall be used as a stored-energy source for the specified UPS system.  The battery shall be housed in separate replaceable modules that slide into any open bay of the UPS cabinet or external battery cabinets, and sized to support the inverter at rated load and power factor, in an ambient temperature between 20° and 25° C, for an xx minutes reserve time.  The expected life of the battery shall be 3 to 5 years or a minimum 250 complete discharge cycles.  For extended battery reserve time, additional battery modules may be added, if the frame size allows, external battery cabinets shall be also be available as an option.

  - COMMUNICATIONS

The UPS shall allow for flexibility in communications.  The UPS shall be able to communicate through two communications ports simultaneously; the media of either communications port may change without affecting the operation of the UPS.  The use of relay contacts shall not affect the operation of the two communications ports.

2.3.1	Relay Contacts

The relay contacts (rated 60 VAC max. and 500 mA max) shall be available
 		through Phoenix Spring terminals with wires sizes of max. : 0.5 mm2

The UPS shall communicate via relay contact closure the following information:

NO 	MAINS_OK Mains Present

NC 	ALARM Mains Failure

C 	Common

NO 	LOAD_ON_INV Load on Inverter

NC 	Message (Load on Mains bypass)

C 	Common

NO 	BATT_LOW Battery Low

NC 	ALARM Battery OK

C 	Common

NO 	LOAD_ON_MAINS Load on bypass (Mains)

NC 	Message (Load on Inverter)

C 	Common

NO 	COMMON_ALARM Common Alarm (System)

NC 	ALARM NO Alarm Condition

C 	Common

    - Serial Communications

The UPS shall be able to communicate through RS232 and USB.

2.3.3	Network Communications

The user shall have the option of installing an optional SNMP card to provide SNMP communication over a local area network. 10/100Mbit Ethernet support shall be included.

2.3.4	UPS Status Information

The software shall be able to retrieve status information present in the UPS. Retrieval of data shall be through either serial communications or through a network connection.

2.5	ACCESSORIES (OPTIONAL COMPONENTS)

2.5.1	External Battery Cabinets

The UPS shall have the capability to add external battery cabinets to the base product. These external battery cabinets with front access battery terminals shall be installed in parallel to provide backup times as required. The connections between the UPS and the extended battery cabinets shall contain DC power only. All of these shall be able to be connected or disconnected safely by the user without interrupting power to the load.

    - Modular Extended Battery Cabinets

The Modular Battery Cabinet shall be pre-configured with Battery trays Modules installed.

3.0 FIELD SERVICES (OPTIONAL)

3.1	FIELD QUALITY CONTROL

The following inspections and test procedures shall be performed by factory trained field service personnel during the UPS start-up.

3.1.1	Visual Inspection

A.	Inspect equipment for signs of shipping or installation damage.

B.	Verify installation per drawings.

C.	Inspect cabinets for foreign objects.

D.	Verify neutral and ground conductors are properly sized and configured.

3.1.2	Mechanical Inspection

A.	Check all power modules are correctly fitted.

B.	Check all battery modules are correctly fitted.

C.	Check all terminal screws, nuts, and/or spade lugs for tightness.

3.1.3	Electrical Inspection

A.	Confirm input voltage and phase rotation is correct.

B	Verify bypass voltage jumper is correct for voltages being used.

3.2	UNIT START-UP AND SITE TESTING

The manufacturer’s field service personnel shall provide site testing if requested.  Site testing shall consist of a complete test of the UPS system and the associated accessories supplied by the manufacturer.  A partial battery discharge test shall be provided as part of the standard start-up procedure.  The test results shall be documented, signed, and dated for future reference.

3.3	MANUFACTURER'S FIELD SERVICE

3.3.1	 Service Personnel

The UPS manufacturer shall directly employ a nationwide service organization, consisting of factory trained Customer Engineers dedicated to the start-up, maintenance, and repair of UPS and power equipment.  The organization shall consist of factory-trained Customer Engineers working out of District Offices in most major cities.  An automated procedure shall be in place to insure that the manufacturer is dedicating the appropriate technical support resources to match escalating customer needs.

The manufacturer shall provide a fully automated national dispatch centre to coordinate field service personnel schedules.  One toll-free number shall reach a qualified support person 24 hours/day, 7 days/week, and 365 days/year.  If emergency service is required, call back response time from a local Customer Engineer shall be xx minutes or less.

3.3.2	Replacement Parts Stocking

Parts shall be available through an extensive network to ensure around- the-clock parts availability throughout the country.

Local Customer Engineers shall stock replacement spare parts with back up available from District Service offices and the manufacturing location.

Customer Support Parts Coordinators shall be on-call 24 hours a day, 7 days a week, and 365 days a year for immediate parts availability.

3.3.3	UPS Maintenance Training

Maintenance training courses for customer employees shall be available by the UPS manufacturer.  This training is in addition to the basic operator training conducted as a part of the system start-up.

The training course shall cover UPS theory, location of subassemblies, safety, battery considerations and UPS operational procedures.  The course shall include AC to DC conversion and DC to AC inversion techniques as well as control and metering, Troubleshooting and fault isolation using alarm information and internal self-diagnostics shall be stressed.

3.3.4	Maintenance Contracts

A complete offering of preventive and full service maintenance contracts for both the UPS system and battery system shall be available.  An extended warranty and preventive maintenance package shall be available.  Warranty and preventive maintenance service shall be performed by factory trained Customer Engineers.