Text for tenders, Rittal PDU basic

Product description

Compact power distribution system for use in IT servers and network enclosures. Vertical mounting using the universal support (supplied) for common IT racks. Suitable for tool-less, fast assembly in Rittal TS IT racks, by means of special “Plug&Play” fastening system (also supplied).

Sturdy aluminium enclosure with fixed output slots (EN60320/C13 or EN60320/C19, depending on the type). The output slots can be protected with a latch to prevent inadvertent cable withdrawal. Unused slots can be closed with covers. This prevents the inadvertent overloading of individual phases and circuits. The circuits/phases are marked in colour with multiphase PDU versions. Depending on the version, a fixed connection cable with a CEE connector is installed, so that the PDU is immediately ready for use.

The warranty period is 24 months during normal operation as intended.

Technical specifications of the “PDU basic”

Input voltage range (L-N):					90 V – 260(400) V AC, 50-60 Hz

Input current:							32 A

No. of phases:							1

Marking of the phases, (3-phase PDUs only: L1, L2, L3):	Brown, black, grey
Number of slots, type EN60320/C13 (total):			24

Number of slots, type EN60320/C13 (per phase/fuse):		12

Number of slots, type EN60320/C19 (total):			4

Number of slots, type EN60320/C19 (per phase/fuse):		2

Number of circuit breakers:					2

Electromagnetic circuit breakers:				16 A, type C

PDU input connector:						EN60309 / CEE

Length of the connection cable:					3 m

Connection cable type:						H05-VV

Number of wires:						3

Cable cross section:						4 mm²

PDU enclosure width:						44 mm (1 U)

PDU enclosure depth:						62 mm

PDU enclosure height:						1115 mm

PDU material:							Aluminium, anodized, RAL 9005 (black)

PDU mounting adapter 						Plastic, black

Conformity:							CE

Standards:

Safety:								EN 60950-1

Safety guideline:						2006/95/EC

MTBF (at 40°C)							80,000 hours

Protection category:						IP 20 (EN 60529)

Protection category:						Class 3

Level of contamination:						2

Overvoltage class:						II

Environmental properties: 					RoHS

Storage temperature 						-25°C to +70°C

Ambient temperatures 						0°C to +45°C

Relative humidity 						10 to 95% RH, non-condensing

Connector locking C13 and C19 				1x (further optional DK 7955.020)

C13 covers in range of goods supplied:				8x (further optional DK 7955.010)

C19 covers in range of goods supplied:				2x (further optional DK 7955.015)

Warranty:							24 months

Type:	Rittal PDU basic, Model No.: DK 7955.111